## Sheet1
WATER PLAN CHECK LIST
| CHECKED BY: |  | TRACT/MAP NO
| EMAIL: |  | PHONE NO.
| SUBMITTED BY: |  | PLAN CHECK DATES
|  |  | 1ST | 2ND | 3RD
DATE RECEIVED
PLANS DISTRIBUTED FOR REVIEW
DATE RETURNED
TITLE SHEETS
| TITLE BLOCK |  |  |  |  | COMPL
| DRAWING NUMBER/PROJECT NUMBER |  |  |  |  | REVISE
| PROJECT LEGAL DESCRIPTION/ADDRESS, APN, MAP NUMBER, PLAN CHECK NUMBER |  |  |  |  | N/A
PROJECT MAP (SHOW LOCATION OF PROJECT IN RELATIONSHIP TO COUNTY)
VICINITY MAP (SHOW LOCATION OF PROJECT IN RELATIONSHIP TO CITY)
| - | PROJECT SITE WITH MAJOR STREETS NAMED
| - | NORTH ARROW
| - | SCALE
| - | THOMAS BROTHERS PAGE & GRID NUMBER
INDEX/KEY MAP REQUIRED FOR ALL PLANS GREATER THAN ONE PLAN/PROFILE SHEET
| - | SCALE CALLED OUT (MINIMUM 100' SCALE)
| - | SHOW WATER MAINS AND APPURTENANCES
| - | SHOW AGENCY DRAWING NUMBERS ON EXISTING MAINS
| - | LEGEND/NORTH ARROW
| - | SHEET NUMBERS
| - | ADJACENT PROPERTY MAP NUMBERS, APNS, AND RECORDS OF SURVEY
| - | EXISTING AND PROPOSED STREET NAMES
LEGEND/QUANTITIES (SYMBOLOGY AND STANDARDS CALLED OUT PER STD SPEC 1.2)
DESCRIPTION OF WORK TO BE DONE
GRADING PLAN NUMBER
STANDARD GENERAL AND WATER CONSTRUCTION NOTES
TABLE OF CONTENTS/INDEX
BENCHMARKS PER COORDINATE SYSTEM AND DATUM REQUIRED BY AGENCY.
BASIS OF BEARINGS
ENGINEER'S STAMP, DECLARATION OF RESPONSIBLE CHARGE, CONTACT INFORMATION
GEOTECHNICAL ENGINEER'S CERTIFICATION
CONTACT INFORMATION FOR DEVLOPER/PROPERTY OWNER
SIGNATURE BLOCKS FOR AGENCY, FIRE DEPARTMENT, AND CITY OR COUNTY
NOTE STATING THE TIME PERIOD THAT APPROVAL FROM AGENCY IS VALID FOR
UNDERGROUND SERVICE ALERT NOTIFICATION BLOCK
RECORD DRAWING SIGNATURE BLOCK
TYPICAL STREET/EASEMENT CROSS SECTION SHOWING UTILITIES, ROW, AND PAVEMENT
NOTES ON PROPER HANDLING OF ASBESTOS CEMENT PIPE
PLAN AND PROFILE SHEETS
TITLE BLOCK
PLAN SCALE 1"= 40 ', 1" = 20', OR OTHER WITH PRIOR APPROVAL
PLAN AND PROFILE ARE ON SAME SHEET WITH PLAN LOCATED BELOW PROFILE
PLAN CONFORMS TO DRAFTING STANDARDS IN WADG SECTION 1.1 & 1.2
STATIONING WITH 100' INTERVALS LABELED
ALIGNMENT IS TIED TO TWO POINTS ON THE CALIFORNIA COORDINATE SYSTEM
PLAN - EXISTING WATER - MIN. SPACE TO NEW WATER - 10 FT OD TO OD
PLAN - EXISTING SEWER - MIN. SPACE TO WATER - 10 FT OD TO OD
PLAN - EXISTING UTILITIES, STORM DRAINS, WATER, SEWER, AND POWER SHOWN
PLAN - ALL PROPOSED UTILITIES ARE SHOWN
PLAN - TIE IN LOCATIONS TO EXISTING SYSTEM SHOW
| - | SIZE, CLASS, TYPE OF MATERIAL
| - | STATION EQUATION
| - | REFERENCE DRAWING NUMBER
| - | TIE IN DETAILS FOR CONNECTION INCLUDING ELEVATIONS
| - | WORK DONE BY DISTRICT AT DEVELOPERS EXPENSE
PLAN - DISTANCE SHOWN TO UTILITIES AND ROAD/EASEMENT WIDTH FROM CENTERLINE
PLAN - EXISTING EASEMENT DOCUMENT, PM, OR TM NUMBERS
PLAN - NEW EASEMENTS DOCUMENT, PM, OR TM NUMBERS
PLAN - EASEMENTS MIN. 20' WIDE, ADD 10' FOR EACH PIPELINE
PLAN - APNs OF ALL PARCELS, LOT NUMBERS, AND BOUNDARY LINES
PLAN - STREET NAMES
PLAN - WATER LINE SIZE AND CLASS CALLED OUT
PLAN - WATER LINE LOCATED BETWEEN ROAD CENTERLINE AND CURB
PLAN - BLOWOFFS (BO) AT LOW POINTS AND LINE VALVES. UTILIZE HYDRANTS WHEN POSSIBLE
PLAN - AIR RELEASE/VACUUM (AV) AT HIGH POINTS, TEES, CROSSES, LINE VALVES.
PLAN - AVOID AVs AND BOs BY MINOR ADJUSTING GRADING
PLAN - WM BOX, BO, AV NOT IN DRIVEWAY
PLAN - WM BOX, BO, AV AT PROPERTY LINE, BUT WITHIN ROW OR EASEMENT.
PLAN - VALVES AT ALL BRANCHES, TEES, AND INTERSECTIONS OF PIPELINES
PLAN - VALVES AT MAX. OF 1320 LF ON DISTRIBUTION (1000 FOR HIGH DENSITY)
PLAN - VALVES AT MAX. OF 2500 LF ON TRANSMISSION
PLAN - LOOP DISTRIBUTION SYSTEM
PLAN - NORTH ARROW AND SCALE
PLAN - EXTEND PIPELINE BEYOND INTERSECTIONS
PLAN - PIPE DATA TABLE WITH PIPE SIZE, BEARING, MATERIAL, PRESSURE CLASS, AWWA
PLAN - ALL SERVICE LATERALS/APPURTENANCES ARE STATIONED AND 90o TO MAIN
PLAN - STATIONS AT CHANGES IN PIPE SIZE, MATERIAL, AND DIRECTION
PLAN - SERVICE LATERALS ARE DROPPED OFF AT ALL PARCELS W/O WATER SRVC.
PLAN - FIRE HYDRANT FLANGE ELEVATIONS ARE CALLED OUT.
PLAN - WATER SERVICES (2" OR LESS) HAVE SEPARATION > 2'
PLAN - COORDINATES (NORTHING & EASTING) CALLED OUT AT ALL PIPE INTERSECTIONS
PLAN - PROPOSED BUILDING PAD ELEVATIONS
PLAN - BLASTING NOTES ARE LISTED TO PROTECT AGENCY UTILITIES
PLAN - RESTRAINED LENGTH SHOWN ON PLANS FOR RESTRAINED JOINTS
PLAN - THRUST BLOCK DATA SIZED IN ACCORDANCE WITH STD SPEC 5.2
PROFILE - 1" = 4' , 1"= 8', OR PRIOR APPROVAL FOR OTHER
PROFILE - SHOW WATER MAIN SLOPE
PROFILE - STATIONS AND ELEVATIONS AT BOTTOM OF PIPE AT CHANGES IN SLOPE
PROFILE - STATIONS WHERE PIPE CHANGES SIZE, CLASS, AND MATERIAL
PROFILE - LARGE DIAMETER WATER LINE CROSSINGS GET PRECEDENCE OVER SMALL
PROFILE - DEFLECTION COUPLINGS/DI FITTING CALLED OUT AT ALL BENDS
PROFILE - ORIGINAL GROUND LINE OVER PIPELINE
PROFILE - PROPOSED GROUND LINE OVER PIPELINE
PROFILE - HYDRAULIC GRADE LINE PLOTTED OR PRESSURE ZONE CALLED OUT
PROFILE - MINIMUM 3' OF COVER TO TOP OF PIPE
PROFILE - BELOW 8' MAXIMUM ALLOWABLE COVER OF EXISTING/PROPOSED PIPE
PROFILE - BLOWOFF AT LOW POINTS AND HIGH POINTS FOR FLUSHING
PROFILE - AIR/VACS AT HIGH POINTS
PROFILE - CUTOFF WALLS SHOWN FOR SLOPES GREATER THAN 20% PER W-29
PROFILE - SHOW ALL CROSSING PIPELINES ≥8-IN W/ BOTTOM OF PIPE ELEVATION
PROFILE - MINIMUM 12" CLEARANCE WHEN CROSSED BY OTHER PIPES
PROFILE - IF CROSSING LESS THAN 12" ASK DISTRICT FOR DIRECTION
PROFILE - PIPELINE ENCASED IN STL SLEEVE & CONCRETE AT CREEK CROSSINGS.
Notes:
Exceptions:
| Project Manager: |  | Date:
| Dept. Manager |  | Date:
SEWER PLAN CHECK LIST
| CHECKED BY: |  | JOB ORDER
| EMAIL: |  | PHONE NO.
| SUBMITTED BY: |  | PLAN CHECK DATES
|  |  | 1ST | 2ND | 3RD
DATE RECEIVED
DATE RETURNED
PLANS DISTRIBUTED FOR REVIEW
COVER SHEET
| TITLE BLOCK |  |  |  |  | COMPL
| DRAWING NUMBER/PROJECT NUMBER |  |  |  |  | REVISE
| PROJECT LEGAL DESCRIPTION/ADDRESS, APN, MAP NUMBER, PLAN CHECK NUMBER |  |  |  |  | N/A
PROJECT MAP (SHOW LOCATION OF PROJECT IN RELATIONSHIP TO COUNTY)
VICINITY MAP (SHOW LOCATION OF PROJECT IN RELATIONSHIP TO CITY)
INDEX MAP (SHOW SHEET NUMBER FOR EACH PORTION OF PROJECT)
NORTH ARROW AND SCALE
LEGEND/QUANTITIES (SYMBOLOGY AND STANDARDS CALLED OUT PER WAS WI-06)
STANDARD GENERAL AND SEWER CONSTRUCTION NOTES
REFERENCES - WAS STDS, GREENBOOK, REGIONAL STDS
TABLE OF CONTENTS/INDEX
BENCHMARKS PER COORDINATE SYSTEM AND DATUM REQUIRED BY AGENCY.
BASIS OF BEARINGS
ENGINEER'S STAMP, DECLARATION OF RESPONSIBLE CHARGE, CONTACT INFORMATION
CONTACT INFORMATION FOR DEVLOPER/PROPERTY OWNER
SIGNATURE BLOCKS FOR AGENCY, FIRE DEPARTMENT, AND CITY OR COUNTY
NOTE STATING THE TIME PERIOD THAT APPROVAL FROM AGENCY IS VALID FOR
UNDERGROUND SERVICE ALERT NOTIFICATION BLOCK
RECORD DRAWING SIGNATURE BLOCK
TYPICAL STREET/EASEMENT CROSS SECTION SHOWING UTILITIES, ROW, AND PAVEMENT
PLAN AND PROFILE SHEETS
TITLE BLOCK
PLAN SCALE 1"= 40 ', 1" = 20', OR OTHER WITH PRIOR APPROVAL
PLAN - NORTH ARROW AND SCALE
PLAN AND PROFILE ARE ON SAME SHEET WITH PLAN LOCATED BELOW PROFILE
PLAN LINEWHEIGHTS CONFORM TO STD SPEC SECTION 1.2
PLAN STATIONING WITH 100' INTERVALS LABELED
PLAN - EXISTING SEWER - MIN. SPACE TO WATER - 10 FT OD TO OD
PLAN - ALL EXISTING UTILITIES, STORM DRAINS, WATER, SEWER, AND POWER SHOWN
PLAN - ALL PROPOSED UTILITIES ARE SHOWN
PLAN - DISTANCE TO UTILITIES FROM CENTERLINE
PLAN - EXISTING EASEMENT DOC NUMBERS
PLAN - NEW EASEMENTS DOC NUMBERS
PLAN - EASEMENTS MIN. 20' WIDE, ADD 10' FOR EACH PIPELINE
PLAN - APNs OF ALL PARCELS, LOT NUMBERS, AND BOUNDARY LINES
PLAN - STREET NAMES
PLAN - SEWER LINE SIZE, MATERIAL, & SDR (MIN)
PLAN - SEWER LINE LOCATED AT CENTERLINE ON PUBLIC ROADS
PLAN - SEWER LATERALS STATIONS (SL)
PLAN - SEWER LATERALS NOT IN DRIVEWAYS, 5' FROM PL, OR LANDSCAPING
PLAN - SEWER LATERALS TO BE PROVIDED TO ALL PROPERTIES
PLAN - SEWER LATERALS TO EXTEND TO PROPERTY LINE & SHOW CLEAN OUTS
PLAN - MANHOLES NUMBERED - OBTAIN FROM GIS TECH
PLAN - STATION & PROVIDE COORDINATES OF ALL MANHOLES
PLAN - MANHOLE SPACED BELOW MAXIMUM ALLOWED
PLAN - NO CURVED PIPE OR BENDS UNLESS APPROVED BY DISTRICT ENGINEER
PLAN - PROVIDE BOUYANCE CALCULATIONS
PLAN - STUBS TO EXTEND 5 FEET BEYOND MANHOLE
PLAN - STUBS TO EXTEND OUT OF ROADWAY OR INTERSECTION
PLAN - PIPE & LATERAL DATA TABLES
PLAN - LATERAL 4-FEET DEEP AT PROPERTY LINE
PLAN - DEEP CUT LATERAL IF VERT. DIST. BET. MAIN AND FS IS > 12 -FEET
PLAN - LATERALS ARE PERPINDICULAR TO MAIN (EXCEPT CUL-DE-SACS)
PROFILE - MAINTAIN 2% SLOPE FROM PL TO DROP TO MANHOLE, VARY DROP AS NEEDED
PROFILE - 1" = 4', 1"= 8 ' , OR OTHER WITH PRIOR APPROVAL
PROFILE - STATIONS AND INVERT ELEVATIONS (IN AND OUT) AT MANHOLES
PROFILE - TOP OF MANHOLE (RIM) ELEVATIONS
PROFILE - NO GRADE BREAKS WITHOUT A MANHOLE
PROFILE - ORIGINAL GROUND LINE OVER PIPELINE
PROFILE - PROPOSED GROUND LINE OVER PIPELINE
PROFILE - TYPICAL DEPTH 5' TO 14 ' WITHOUT PRIOR AGENCY APPROVAL.
PROFILE - MINIMUM 12" SPACE ABOVE PIPE WHEN CROSSED BY OTHER PIPES
PROFILE - MIN SLOPES - MAINLINES 0.5%, 1% DEAD END STREETS
PROFILE - MAX. SLOPES - 8" (8.3%) - 10" (6.2%) - 12" (4.9%) - OR DROP MANHOLE
PROFILE - PIPES THROUGH CREEK CROSSINGS ENCASED IN STEEL & CONCRETE
PROFILE - SHOW ALL CROSSING PIPELINES OF 8-IN AND ABOVE W/ INVERT ELEV.
PROFILE - MANHOLE DROP 0.20 ' MIN. (PIPES <15") OR FORMULA (PIPES>15")
PROFILE - MINIMUM DEPTH OF MAIN @ FL = 5-FEET
PROFILE - MAXIMUM DEPTH OF MAIN =14-FEET WITHOUT SPECIAL DESIGN
PROFILE - DROP MANHOLE USED IF 2 MAINS HAVE > 3' SEPARATION
PLAN/PROFILE - LATERALS HAVE MIN. 4-FOOT SEPARATION BETWEEN THEM
PLAN/PROFILE - SEWER MAIN CLEANOUT REQD ON DEAD ENDS <150' FROM MH
Notes:
Exceptions:
Date:
Date:
Project Manager:
Dept. Manager